COMPRESSOR PERIODIC MAINTENANCE FORM

Foramen: ..............................    Maintenance Chief: .................................          Date:……........……..................

Compressor working hours: (                        -                        )

| Code | Maintenance area | Job | Mon | Tue | Wed | Thu | Fri | Sat | Responsible |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 101 | Temperature indicator | Check the heat | x | x | x | x | x | x | Foramen |
| 102 | Separator | Check the pressure difference (by hand button) | x | x | x | x | x | x | Foramen |
| 103 | Oil decomposing tank | Discharge the condensed water under the tank |  |  |  |  |  | x | Foramen |
| 104 | Oil decomposing tank | Check the oil level |  |  |  |  |  | x | Foramen |
| 105 | Air suction filter | Check and clean |  |  |  |  |  | x | Foramen |
| 106 | Air filter | Check the filter |  |  |  |  |  | x | Foramen |
| Air Dryer |
| 107 | Condense discharging line | Check for discharging |  |  |  |  |  | x | Foramen |
| 108 | Condenser | Clean with the air |  |  |  |  |  | x | Foramen |

| MAINTENANCE JOBS TO BE DONE FOR EVERY 2.000 HOURS (Service C) |
| --- |
| Oil system | Check the oil | x | Foramen |
| Oil filter | Renew | x | Foramen |
| Skavenç filter | Clean | x | Foramen |
| Blow down system | Check its running | x | Foramen |
| Air filter | Renew | x | Foramen |
| Electrical cables | Check | x | Foramen |
| Oil/Air cooler | Clean | x | Foramen |
| Pressure adjustment gauge | Check its adjustment | x | Foramen |
| Negative regulator | Check zero working pressure | x | Foramen |
| Fan thermostat | Check its running | x | Foramen |
| Poly-V belt | Check | x | Foramen |
| MAINTENANCE JOBS TO BE DONE FOR EVERY 4.000 HOURS (Service D) |
| Additional to service C: |
| Separator | Renew | x | Foramen |
| Oil decomposing tank sealing | Renew | x | Foramen |
| Minimum pressure valve O-rings | Renew the cylinder/valve 0-rings | x | Foramen |
| Air Dryer |
| Oil filter (inlet) | Renew | x | Foramen |
| Water filter (outlet) | Renew | x | Foramen |
| MAINTENANCE JOBS TO BE DONE FOR EVERY 8.000 HOURS (Service E) |
| Additional to service D: |
| Main button group | Check the contactor and its connections | x | Foramen |
| Suction regulator | Renew diaphragm and sealing. Check all movable parts (bushing, spring, sealing, o-ring) | x | Foramen |
| Shortcut circuit valve | Check diaphragm, cylinder, o-ring, spring, bushing, sealing | x | Foramen |
| Minimum pressure valve | Check the springs | x | Foramen |
| Oil/Air cooler | Clean | x | Foramen |
| Poly-V bet | Renew | x | Foramen |
| MAINTENANCE JOBS TO BE DONE FOR EVERY 20.000 HOURS (Service F) |
| Additional to service E: |
| Screw bearings and sealing | Renew | x | Foramen |
| All hoses, sealing, and O-rings | Renew | x | Foramen |
| Motor bearings | Renew | x | Foramen |