FIRE TYPES AT MATCH FACTORY

AND INTERVENTION METHOTS

(08 October 2007)

Prepared by: Bilal Bilici

- Inspection Table:

This is most frequently fire type that comes across the line. Since this small fire can be seen by Inspection Table operator, first intervention must be done by her. Waste matches can burn because of friction inside recycle box. It can be extinguished by pouring small amount of water. Outer Table operator has to intervene the fire by taking water bucket below the wall.

For precautions, at least 6 buckets must always be kept full with water standing under the wall.

For precautions, do not let big amount of waste on the floor and in the recycle box.

2) Front Fire (ROG2):

In case of fire starting from bar mat in front of ROG4 unit, intervent immediately by using extinguisher. Fire intervention points should be in front of ROG4 and top of KU5 conveyor. Since automatic steam fire extinguisher system will work, so be quiet during intervention.

After extinguishing the fire open gates for air ventilation.

After extinguishing, renew mobile fire extinguisher if used.

3) Dipping Table Fire:

Dipping unit is the most dangerous place for fire. The main danger is the fire to spread to whole bars. That’s why on the dipping conveyor we have to keep both side wet and provide air-water spray working all times. Normally automatic steam fire extinguisher system will work immediately. But be prepared to intervene by mobile fire extinguisher.

After use, renew the extinguishers.

4) Paraffin Table Fire:

Paraffin in the table is heated both steam pipe and electrical heater resistance. When the paraffin level is reduced below heat exchanger or resistance, fire risk happens due to contact with air. If melted paraffin ignites, operators at inspection and KU1 conveyor should intervene the fire immediately by using dry chemical powder extinguisher. Never use water for paraffin extinguishing.

In case of paraffin fire, shout down paraffin feeding pump and electrical heater resistance.

After use, renew the extinguishers.

5) Head Composition Unit Fire:

In this unit fire risk is very low. But dry deposits and built up remain at the side of buckets or mixers (due to weak cleaning), ignition can cause in case of any friction. But this kind of fire is small so can be extinguished easily by the operators.

9) Electrical Fire:

Electrical main panels and power switches should be used by only electrical technicians. In case of any fire or ignition due to button, switch and transformer system, only permit electrical technicians to intervene. They have to shout down the power immediately. If fire continues, apply fire extinguisher. Do not use chemical powder extinguisher at electrical fires.

11) Finished Goods Warehouse Fire:

First intervention should be done by the operator in warehouse.

According to severity of fire, hydrant and hose systems can be used. After killing fire, cartons should be taken out from the place immediately to ensure rest of cartons is safe.

In order to avoid spreading to another division, the compartments should be divided by steel and insulated door. While loading the finished good warehouse the front of fire hydrants should be kept empty in case of use.

Cartoons should be so located that they will not touch electrical buttons and cables. Their height should not exceed 1 meter to sprinkler pipe installation.

12) Chemical Raw Material Warehouse Fire:

The chemical materials should be stored separately to ensure them not being affected from each other. The doors should always be kept locked and authorized personnel should open it. The stores should be forbidden for fire and smoke. Dry grasses s around stores should be trimmed frequently to avoid fire.

NOT: All fires and incidents have been reported by Shift in Charges after shifting. They have to full report form including investigating the reasons and measures since. A copy of the report should be submitted to top Management and a copy should be hanged on the information table (Occupational Health & Safety Information Table) for the employees to know and be careful in future regarding the fire.